## General Data
Plant: Solar-System for different locations in Haiti
Date: | 2009-12-08
System-voltage (12V/24V): |  | 12 | V | Country-voltage (110V/220V) |  | 110 | V
8 houses should be equipped with a Battery-Backup-System with Solar in order to reduce fuel-cost
The project should be proceeded in 2 Steps
Batteries are charged by Solar and Generator and Mains with a 30 A Charger
cable-lenght Solar-Paneel to Charge-Controller: |  |  |  |  | m
cable-lenght Generator to Cabinet |  |  |  |  | m
Contact:
Stefan Schranner
Alternative Technologie
Franz-Ludwig-Str.2
97072 Würzburg
Tel: +49 (0)931 72353
Mobil: +49 (0)170 6343070
Internet: www.alternative-technologie.de
Email: StefanSchranner@yahoo.de
Select here the subsequent Plans!

## List of Items
Calculation Solar-System Haiti
all prices in Euro!
Input Data | Calculations=
|  | Picture | Units | Price/Unit(Euro) | Price (Euro) | Order-Nr | from where? | Comment
Installation
Lamps 13W110/220V |  |  | 0 | 3.95 | 0 | Neolux 13 E27 | www.reichelt.de | Haiti
Lamps 17W110/220V |  |  | 0 | 4.7 | 0 | Neolux 17 E27 | www.reichelt.de | Haiti
Lamp 15W with Sensor |  |  | 0 | 15.35 | 0 | Dulux 15-Sensor | www.reichelt.de | Haiti
0
Sockets Lamps 110/220V |  |  | 0 | 1.15 | 0 | Fassung E14 | www.reichelt.de | Haiti
0
Light Switches |  |  | 0 | 2.4 | 0 | EL FR WS | www.reichelt.de | Haiti
or Moving-Detector |  |  | 0 | 8.95 | 0 | 50-520 121 | www.pollin.de
Sockets 110/220V |  |  | 0 | 1.95 | 0 | EL FR SKDO 1 | www.reichelt.de | Haiti
0
Installation-Cable indoor NYM, J3*1,5 10m |  |  | 5 | 6.55 | 32.75 | NYM, J3*1,5 10m | www.reichelt.de
0
Installation-Cable Outdoor NYY-J 3*1,5 25m |  |  | 0 | 21.3 | 0 | NYY-J 3*1,5 25m | www.reichelt.de
0
Clamps for cable inhouse with Nails |  |  | 1 | 3.75 | 3.75 | Isoschelle 7-11 | www.reichelt.de
0
Nails for clamps |  |  | 1 | 1 | 1 | integrated in Isoschelle | www.reichelt.de
0
Power-Switch 1NC, 1NO, 220V coil (Generator direct to Load etc) |  |  | 8 | 30 | Spende |  | www.Ebay.de
FI-Switch |  |  | 0 | 31.5 | 0 | EL FI2 2503 | www.reichelt.de
0
Fuses 6A |  |  | 0 | 7.1 | 0 | EL LSCO B 6A | www.reichelt.de
Terminals |  |  | 0 | 0.64 | 0 | WAGO 280-901 | www.reichelt.de
Cable-binder 100pcs |  |  | 1 | 0.41 | 0.41 | KAB 100-2,5 | www.reichelt.de
Junction-Box for Terminals, Switch etc |  |  | 0 | 54 | 0 | Bopla RCP 310F | www.reichelt.de
Small box for Fuse and Switch etc 160*140*140 |  |  | 8 | 4.95 | 39.6 | EL KV06 | www.reichelt.de
Installation and Lamps |  |  |  |  | 77.51
Inverter
Sinus Inverter 12V/110V 1200VA |  |  | 8 | 356.3 | Spende | SWR 12-1200 | www.reichelt.de | Haiti
Spare-Fuses for the Inverter |  |  | 0 | 0.5 | 0 | check value! | www.reichelt.de
Plug 110V Inverter |  |  | 8 | 0.57 | Spende | SST 1 ws | www.reichelt.de | Haiti
3 connection Power-Point/Socket |  |  | 0 | 1.25 | 0 | 3-fach Dose BR | www.reichelt.de
Cable Inverter ->Battery red (normally shipped w.Inverter) 5m |  |  | 0 | 1.6 | 0 | FLK 6,0 RT-5 | www.reichelt.de | This is 6 qmm; to get 16 qmm take it several times
Cable Inverter ->Battery black (normally shipped w.Inverter) 5m |  |  | 0 | 1.6 | 0 | FLK 6,0 SW-5 | www.reichelt.de | This is 6 qmm; to get 16 qmm take it several times
Battery-Charger for the Generator |  |  | 0 |  | 0
Victron Centaur Charger 12V/30A analog 110/220V, Lead-acid, Gel or AGM |  |  | 0 | 271 | 0 |  | http://www.ferroberlin.de/ferroberlin2/product_info.php/info/p196_victron-ladegeraet-centaur-charger-12v---30a--3-.html
Sterling Pro Charge Digital Ladegerät 1230CED 30 A |  |  | 8 | 280 | 2240 |  | http://www.bootdepot.de/1284-elektronik/220-gps--funk--elektronik/1311-ladegeraete/1310-sterling-ladegeraete--laderegler/1313-sterling-pro-charge-serie/8832-sterling-pro-charge-ladegeraet-pc-1230-30-a-.html?from=froogle
Spare-Fuses for the Charger |  |  | 0 | 0.5 | 0 | check value! | www.reichelt.de
Cable Generator->Charger; 25m (lenght to Generator), outdoor |  |  | 2 | 21.3 | 42.6 | NYY-J 3x1,5 25m | www.reichelt.de
Cable Charger ->Battery red |  |  | 0 | 5.85 | 0 | FLK 6,0 RT-5 | www.reichelt.de | This is 6 qmm; to get 16 qmm take it several times
Cable Charger ->Battery black |  |  | 0 | 5.85 | 0 | FLK 6,0 SW-5 | www.reichelt.de | This is 6 qmm; to get 16 qmm take it several times
Batteries
Sonnenschein dryfit Solar Gel 12V 90 Ah |  |  | 16 | 190 | 3040 |  | http://www.solarstrom.net/batterien.htm
Sonnenschein dryfit Solar Gel 12V 130 Ah |  |  | 0 | 296 | 0 |  | http://www.solarstrom.net/batterien.htm
Sonnenschein dryfit Solar Gel 12V 230 Ah |  |  | 0 | 498 | 0 |  | http://www.solarstrom.net/batterien.htm
Terminals Batteries (Check Terminal-Type) |  |  | 16 | 1.75 | 28 | Batterieklemmen | www.reichelt.de
Inverter and Battery and Charger from Generator |  |  |  |  | 5350.6
Solar-Modules
Schott ASI 95 Wp Dünnschicht |  |  | 8 | 160 | 1280
Accessoires Solar-Modules
Frame for Solar-Paneel (for 2 Paneel) |  |  | 4 | 140 | 560 | Schletter FixZ-7 | www.solarsysteme-mittermeier.de
including Protection against stealing: secufix-System to fix the screews |  |  | 0 | 50 | 0 | Schletter secufix
or put Epoxy on top of the screws or remove the slot
Screws etc. for Mouting |  |  | 0 | 10 | 0
Cable Solar-Panel->Charge-Controller, per m*2 (multiply with length and 2 for + and -) |  |  | 100 | 1.55 | 155 | Titanex Solarkabel 1 x 10 mm² per Meter
or Lapptherm Solar |  |  | 0 |  | 0 |  | www.conrad.de
Charge-Controller
Metamorphosis 30A, with Alarm-System, 5 Load Channels, Generator Start/Sop and more |  |  | 4 | 199 | Spende | Metamorphosis | www.alternative-technologie.de
|  |  | 0 |  | 0
Cable Charge-Controller ->Battery red 5m |  |  | 0 | 1.6 | 0 | FLK 6,0 RT-5 | www.reichelt.de | This is 6 qmm; to get 16 qmm take it several times
Cable Charge-Controller ->Battery black 5m |  |  | 0 | 1.6 | 0 | FLK 6,0 SW-5 | www.reichelt.de | This is 6 qmm; to get 16 qmm take it several times
Solar-Modules and Charger |  |  |  |  | 1995
Alarm-System
Moving-Detector 12 V |  |  | 4 | 24.6 | Spende | IR-Melder 12V | www.reichelt.de
Moving-Detector 110V or 220 V |  |  | 0 | 8.95 | 0 | 50-520 121 | www.pollin.de | Haiti
Alarm-Horn 12V, Outdoor-Type |  |  | 0 | 7.95 | 0 | 50-850 375 | www.pollin.de
Alarm-Horn 12V, outdoor, very loud |  |  | 4 | 13.25 | 53 | BS 12 | www.reichelt.de
Alarm-Light 12V-Lamp, Outdoor-Type |  |  | 0 |  | 0
High-Voltage-Generator |  |  | 0 | 17 | 0 | Kemo M062
Wire 2*0,5 mm, 10m |  |  | 4 | 1.25 | 5 | LA 205-10
Alarm-System Total |  |  |  |  | 58
Tools
Battery-Powered Drilling Machine |  |  |  |  | Spende |  |  | Haiti
red adhesive Tape for marking + | [7 empty] | Haiti
cable end terminals
Tool for cable end terminals
Epoxyd-Harz
200
Transportation Batteries |  |  |  |  | 193
Total |  |  |  |  | 7874.11
No cost for Post-Delivery, Packing and Customs included!